## Domestic Water
20-Q061 331 COOPER
Domestic water flow | GPM | #N/A
Domestic water required boost pressure | PSI
Boundary Conditions (From Civil)
[8 empty] | WSFU | GPM | GPM | Diam
DOMESTIC WATER DEMAND | [7 empty] | 1 | 3 | 1.7 | 0.5
[8 empty] | 2 | 5 | 3.5 | 0.75
PHASE 1 | [7 empty] | 4 | 8 | 7 | 1
Plumbing Fixtures | Qty | DCW F.U. | DCW Total | DHW F.U. | DHW Total | Combined F.U. | Total | 8 | 12.8 | 14 | 1.25
Residential | [7 empty] | 15 | 17.5 | 20 | 1.5
Full Washroom | 0 | 2.7 | 0 | 1.5 | 0 | 3.6 | 0 | 30 | 23.3 | 40 | 2
1/2 Washroom | 0 | 2.7 | 0 | 1.5 | 0 | 3.1 | 0 | 50 | 29.1 | 75 | 2.5
Kitchen Sink | 0 | 1 | 0 | 1 | 0 | 1.4 | 0 | 60 | 33 | 120 | 3
Dishwasher | 0 | 0 | 0 | 1.4 | 0 | 1.4 | 0 | 70 | 37 | 250 | 4
Clothes washer | 0 | 1 | 0 | 1 | 0 | 1.4 | 0 | 80 | 40 | 750 | 6
Total PODs |  |  | 0 |  | 0 |  | 0 | 90 | 42
Common | [7 empty] | 100 | 45
Full Washroom | 0 | 2.7 | 0 | 1.5 | 0 | 3.6 | 0 | 110 | 47
1/2 Washroom | 0 | 2.7 | 0 | 1.5 | 0 | 3.1 | 0 | 120 | 49
Hand Sink | 0 | 1.5 | 0 | 1.5 | 0 | 3 | 0 | 130 | 51
Kitchen Sink | 0 | 3 | 0 | 3 | 0 | 4 | 0 | 140 | 53
Dishwasher | 0 | 0 | 0 | 1.4 | 0 | 1.4 | 0 | 150 | 55
Clothes washer | 0 | 3 | 0 | 3 | 0 | 4 | 0 | 160 | 58
Hose Bib 1/2" | 0 | 2.5 | 0 | 0 | 0 | 2.5 | 0 | 170 | 60
Hose Bib 3/4" | 0 | 3 | 0 | 0 | 0 | 3 | 0 | 180 | 62
Janitor Sink | 0 | 2.25 | 0 | 2.25 | 0 | 3 | 0 | 190 | 65
Urinal | 0 | 1.5 | 0 | 1.5 | 0 | 2 | 0 | 200 | 67
Total Common | - | - | 0 | - | 0 | - | 0 | 210 | 68.5
Kitchen | [7 empty] | 220 | 70
Sink #8 | 0 |  |  |  |  | 1.5 | 0 | 230 | 72
Scullery #10 | 0 |  |  |  |  | 1.6 | 0 | 240 | 75
Dishwasher #15 | 0 |  |  |  |  | 0.9 | 0 | 250 | 78
Dishtable #16 | 0 |  |  |  |  | 1.6 | 0 | 300 | 80
Sink #19 | 0 |  |  |  |  | 1.5 | 0 | 400 | 110
Scullery #21 | 0 |  |  |  |  | 1.6 | 0 | 500 | 125
Dispenser #31 | 0 |  |  |  |  | 0.07 | 0 | 600 | 150
Sink #34 | 0 |  |  |  |  | 1.5 | 0 | 700 | 170
1/2 Washroom | 0 |  |  |  |  | 3.1 | 0 | 800 | 180
Total Kitchen | [5 empty] | - | 0 | 900 | 200
Maximum demand |  | FU | 0 | - | 0 | - | 0 | 1000 | 220
Diversity |  | 100% | [5 empty] | 1250 | 250
Calculated demand |  | FU | 0 | - | 0 | - | 0 | 1500 | 270
Water supply flow |  | GPM | #N/A | - | #N/A | - | #N/A | 1750 | 300
Water supply pipe size |  | in | #N/A | - | #N/A | - | #N/A | 2000 | 330
[8 empty] | 2250 | 350
[8 empty] | 2500 | 380
[8 empty] | 2750 | 400
[8 empty] | 3000 | 430

## Riser Size Calculator
WSFU | GPM
1 | 3
2 | 5 |  | INPUTS |  | OUTPUTS |  |  |  | Total Demand: |  |  |  | Notes:
4 | 8 |  |  | Supply |  | Volume | Size | Pipe Size Transition | DO NOT EDIT
8 | 12.8 | FLOORS |  | Fixture Units supplying |  | Flow Rate | Diameter |  | DHW: | FU | 0
15 | 17.5 |  |  | FU |  | GPM | NPS | Yes/No |  | GPM | #N/A
30 | 23.3 |  | 9 | 97 |  | 44.1 | 3 |  |  | Supply Pipe Size | #N/A
50 | 29.1 |  | 9 | 88 |  | 41.6 | 3 |  | DCW: | FU | 0
60 | 33 |  | 9 | 79 |  | 39.7 | 3 |  |  | GPM | #N/A
70 | 37 |  | 9 | 70 |  | 37 | 2.5 | Pipe transition needed |  | Supply Pipe Size | #N/A
80 | 40 |  | 9 | 61 |  | 33.4 | 2.5 |  | Combined: | FU | 0
90 | 42 |  | 9 | 52 |  | 29.88 | 2.5 |  |  | GPM | #N/A
100 | 45 |  | 9 | 43 |  | 27.07 | 2.5 |  |  | Supply Pipe Size | #N/A
110 | 47 |  | 9 | 34 |  | 24.46 | 2 | Pipe transition needed
120 | 49 |  | 5 | 25 |  | 21.3667 | 2 |  | Residential | DCW | DHW | Combined
130 | 51 |  | 5 | 20 |  | 19.4333 | 1.5 | Pipe transition needed | Full Washroom | 2.7 | 1.5 | 3.6
140 | 53 |  | 5 | 15 |  | 17.5 | 1.5 |  | 1/2 Washroom | 2.7 | 1.5 | 3.1
150 | 55 |  | 5 | 10 |  | 14.1429 | 1.25 | Pipe transition needed | Kitchen Sink | 1 | 1 | 1.4
160 | 58 |  | 5 | 5 |  | 9.2 | 1 | Pipe transition needed | Dishwasher | 0 | 1.4 | 1.4
170 | 60 | [7 empty] | Clothes washer | 1 | 1 | 1.4
180 | 62 |  | 9 | 97 |  | 44.1 | 3 | Pipe transition needed
190 | 65 |  | 9 | 88 |  | 41.6 | 3 |  | Common | DCW | DHW | Combined
200 | 67 |  | 9 | 79 |  | 39.7 | 3 |  | Full Washroom | 2.7 | 1.5 | 3.6
210 | 68.5 |  | 9 | 70 |  | 37 | 2.5 | Pipe transition needed | 1/2 Washroom | 2.7 | 1.5 | 3.1
220 | 70 |  | 9 | 61 |  | 33.4 | 2.5 |  | Hand Sink | 1.5 | 1.5 | 3
230 | 72 |  | 9 | 52 |  | 29.88 | 2.5 |  | Kitchen Sink | 3 | 3 | 4
240 | 75 |  | 9 | 43 |  | 27.07 | 2.5 |  | Dishwasher | 0 | 1.4 | 1.4
250 | 78 |  | 9 | 34 |  | 24.46 | 2 | Pipe transition needed | Clothes washer | 3 | 3 | 4
300 | 80 |  | 5 | 25 |  | 21.3667 | 2 |  | Hose Bib 1/2" | 2.5 | 0 | 2.5
400 | 110 |  | 5 | 20 |  | 19.4333 | 1.5 | Pipe transition needed | Hose Bib 3/4" | 3 | 0 | 3
500 | 125 |  | 5 | 15 |  | 17.5 | 1.5 |  | Janitor Sink | 2.25 | 2.25 | 3
600 | 150 |  | 5 | 10 |  | 14.1429 | 1.25 | Pipe transition needed | Urinal | 1.5 | 1.5 | 2
700 | 170 |  | 5 | 5 |  | 9.2 | 1 | Pipe transition needed
800 | 180
900 | 200
1000 | 220
1250 | 250
1500 | 270
1750 | 300
2000 | 330
2250 | 350
2500 | 380
2750 | 400
3000 | 430

## Hydronics
Required GPM | PIPE SIZE (NPS) | Notes:
Hydronics Pipulator - as per the OBC -